## Slide 1
BLUESUN 1WM/2MWH
ENERGY STORAGE SYSTEM

## Slide 2
2
CHAPTER
01
Product Sepcification
03
Technical Proposal
02
全球布局
System function
Mission
Enable green energy to create a zero-carbon ecology
Vision
To become a world-class leader in energy technology innovation
Value
Adhere to the right innovation practice and smooth

## Slide 3
01 System Configure
The system application scenario is solar energy storage system self-using.
Initial Configuration | 
PV power | 1MW
Energy storage system | 2MWH
AC power output | 1MW
The requirement for the battery system is 1 MW 2 MWh available.
The system will output 400 V AC voltage.
For this system, we provide the a all-in-one Liquid cooling battery as proposal.
1MW/2MWh
400V

## Slide 4
01 Main device List
Specification |  | Qty | Unit | Item
PV panel 610W solar panel | Half cell topcon | 1638 | piecess | 
DC combiner box | 12 lines in and 12 lines out | 8 | pieces | 
Solar panel rack |  | 1 | set | 
ON-grid string inverter 125KW |  | 8 | pieces | 
125KW/261KWH energy storage system cabinet | 166.4V 314AH lithium battery moudle including BMS | 5 | pieces | 
 | High voltage control box | 1 | piece | 
 | Liquid cooling machine | 1 | piece | 
 | 125KW PCS | 1 | piece | 
 | Fire protection system | 1 | set | 

## Slide 5
300+
Projects completed
18+million
Cells analyzed
15+GWh
Deployed
0
Safety issues
3
01 Degradation Table
BATTERY SIZING CALCULATION AND CAPACITY PROFILE FOR 10YEARS (FOR 1 MW / 2.08MWh BESS) |  |  |  | 
Year | Designed Gross Battery Capacity | Degradation for 1 Cycle/day) | AC Output Efficiency | Total AC Usable Cap.(MWh)
Year 0 | 2.08 | 98.40% | 85.06% | 1.77
Year 1 | 2.08 | 92.01% | 83.05% | 1.72
Year 2 | 2.08 | 88.03% | 82.26% | 1.71
Year 3 | 2.08 | 85.32% | 81.57% | 1.69
Year 4 | 2.08 | 84.06% | 80.95% | 1.68
Year 5 | 2.08 | 82.75% | 80.35% | 1.67
Year 6 | 2.08 | 81.57% | 79.78% | 1.66
Year 7 | 2.08 | 80.35% | 79.22% | 1.64
Year 8 | 2.08 | 79.13% | 78.66% | 1.63
Year 9 | 2.08 | 77.91% | 78.12% | 1.62
Year 10 | 2.08 | 76.69% | 77.57% | 1.61

## Slide 6
01 Installation oversee

## Slide 7
01 Schematic diagram

## Slide 8
Module Type | BSM610M10-78HNH | 
Maximum Power(Pmax/W) | STC | NMOT
 | 610 | 461
Operating Voltage | 50.34 | 48.05
Operating Current (Imp/A) | 15.47 | 12.50
Open-Circuit Voltage (Voc/V) | 41.58 | 39.02
Short-Circuit Current (Isc/A) | 14.66 | 11.83
Moudle Efficiency ηm(%) | 23.61 | 
Power Gain | 5% | 
Maximum Power (Pmax/W) | 641 | 
Module Efficiency(η/%) | 24.79 | 
Power Gain | 15% | 
Maximum Power (Pmax/W) | 671 | 
Module Efficiency(η/%) | 25.98 | 
Cell Type | N-type Topcon | 
Cell Arrangement | 132(6*22) | 
Weight | 32.5kg | 
Module Dimensions | 2278*1134*30mm | 
Maximum System Voltage | 1500V DC(IEC) | 
Operating Temperature | -40°C~ +85°C | 
Maximum Series Fuse | 30A | 
Static Loading | Snow Loading: 5400Pa/ Wind Loading: 2400Pa | 
02 PV panel

## Slide 9
02-1 125KW ON-grid string inverter
Model | BSM125K-B |  | 
Input(DC) | Max.DC Voltage |  | 1100V
 | Max.Input Current Per MPPT |  | 40A
 | Max.Short-circuit Current Per MPPT |  | 60A
 | Start Voltage |  | 350V
 | MPPT Voltage Range |  | 200-1000V
 | Nominal Voltage |  | 650V
 | Number of MPPT | 8 | 
 | Strings Per MPPT | 2 | 
Output(AC) | Nominal AC Output Power | 125KW | 
 | Max. AC Output Power | 125kVA | 
 | Nominal AC Voltage | 230V/400V,3W+PE,3W+N+PE | 
 | AC Grid Frequency Range | 50Hz / 60Hz(±5Hz) | 
 | Max. Output Current | 181.2A | 
 | Power Factor(Φ) | 0.8leading-0.8lagging | 
 | THDi | ＜3%（Nominal Power） | 
Efficiency | Max. Efficiency | 98.7%
 | Euro Efficiency | 98.3%
 | Dimensions W x H x D | 965mm*700mm*355mm
 | Weight | 85kg

## Slide 10
02 125KW/261KWH ENERGY STORAGE SYSTEM
125KW 261KWH ENERGY STORAGE SYSTEM |  |  | 
NO | Item |  | Specification
Battery Side |  |  | 
1 | Configuration |  | 1P260S
2 | Rated Energy |  | 261kWh
3 | Rated Voltage |  | 832VDC
4 | Voltage Range |  | 728~936VDC
5 | Charging/Discharging Current | Rated | 157A
 |  | Maximum | 314A
6 | General Parameters | Size | 1005(L)*1320(W)*2200(H)
 |  | Weight | 2.5T
 |  | IP Level | IP66
 |  | Cooling mode | Liquid Cooling
 |  | Communication agreement | CAN
 |  | Coolant | 50% Ethylene glycol aqueous solution
AC Side (Grid Connection) |  |  | 
Rated Voltage(V) |  | 230/400 | 
AC Output Type |  | (3W + N + PE) three-phase four line | 
Rated Output Power(KW) |  | 125 | 
Rated Grid Frequency(Hz) |  | 50/60 | 
AC Side (off-grid) |  |  | 
Rated Output Voltage |  | 230/400 | 
Rated Output Power |  | 125 | 
Maximum Apparent Power (KW) |  | 138 | 
Maximum Output Current (A) |  | 200 | 
Chiller
fire protection
control box
Battery Module
PCS
EMS
Dehumidifier

## Slide 11
02 EMS
Input platform - the browser address: https://www.iesscloud.com/#/ can enter the login page
(it is recommended to use chrome), enter the corresponding user name and password to log in.
Testing account: BS@test.com
Password: 123456
To create a new account, the platform administrator needs to add it in [System Management]
-- [Account Settings]

## Slide 12
03 System Function
· PV absorption
Under the current situation, the installed capacity of photovoltaics in the region has reached saturation. During the peak period of photovoltaic power generation, it has an impact on the power grid. Therefore, it is necessary to equip with corresponding energy storage facilities to mitigate the instability of photovoltaic power generation. This set of systems can effectively absorb the electricity generated by photovoltaics during the peak period of photovoltaic power generation and supply power to users through energy storage during the peak period of electricity consumption.
· Peak Shaving and Valley Filling
The local power grid has different electricity prices corresponding to each time period. By using energy storage devices, the battery can be charged from the power grid when the electricity price is at a low stage. And when the electricity price rises to a high stage, the electricity stored in the battery can be discharged for the use of property owners. In this way, the property owners can benefit from the price difference of electricity

## Slide 13
Making energy storage simple
www.bluesunpv . com info@bluesunpv.com
Follow us on LinkedIn
Learn more about Bluesun